## CoverPage
ODO Master Input File - Reference Guide
Operations & Design Optimization for Networked Microgrids
Funded by
Office of Electricity Delivery and Energy Reliability
under Mr. Dan Ton (Program Manager of Smart Grid R&D)
US Department of Energy
Prepared by
National Renewable Energy Laboratory
Collaborators
Los Alamos National Laboratory
Oak Ridge National Laboratory
Pacific Northwest National Laboratory
Sandia National Laboratory

## Introduction
Introduction
This template is intended for use with the Operations and Design Optimization (OD&O) tool v0.3 available via GITHUB (https://github.com/lanl-ansi/ODO). The project has been funded by the U.S. Department of Energy (Office of Electricity Delivery and Energy Reliability) under Mr. Dan Ton (Program Manager of Smart Grid R&D).
The template lists and explains the user inputs necessary for using the OD&O tool for analysis and feasibility of networked microgrids given a particular system. Overall, the inputs are categorized into three types:
[1]. (P)arsed from the power system model
[2]. (U)ser Defined
[3]. (P or U) : When the given input can be provided by either [1] or [2].
The inputs marked as P or U are defined separately because they may or may not be included in the power system model. For example, 'Status' variable (whether the device is connected or not) may not be a part of the model files. Similarly, the Vmin, Vmax limits for the buses are not always included in the model files (e.g. in OpenDSS). In that case, these parameters will need to be externally supplied to provide different scenarios or outer bounds.
All the input parameters are mandatory unless otherwise specified.
Important Note: All the values are provided in per unit unless otherwise specified.
Worksheet - 1. From the Model files [JSON]
These inputs are used to define the input file (in JSON format) containing the power system modeling parameters to the OD&O tool. The respective worksheet '1. From the Model files (JSON)' must be updated to provide the respective default values. Default values are used by the system when a given parameter is not defined exclusively as a user input. For example, if the voltage at a given bus (under steady state power flow) is not stated, the default value provided in the worksheet (generally 1 p.u.) is used.
The DER type (PV/Wind/Others) is not specified in the JSON File - It will be specified in the Output file.
If the system model consists of more than one file, please provide the location of the respective files in the "file location" column w.r.t to parent directory.
The inputs marked as P or U identify the parameters which may or may not be a part of the system model files. The presence of any parameters marked as such should be verified in the power system file. If the parameter is not present (for e.g. generator cost parameters for OpenDSS models), the inputs need to be provided in a separate text file named as 'XXXXX.txt'. Given a parameter 'param1' under 'component', the file would be named 'param1@component.txt' with the inputs available as comma separated values for each component.
Eg. For 'four' branches with respective ampacities, the file will be named as 'current_rating_a@branch.txt'. The input for each branch is a list of 3 values representing the capacity of each phase of the branch. Therefore, the corresponding rows in the file would have the comma separated values as:
name_branch_1,rating_phase_a,rating_phase_b,rating_phase_c
name_branch_2,rating_phase_a,rating_phase_b,rating_phase_c
name_branch_3,rating_phase_a,rating_phase_b,rating_phase_c
name_branch_4,rating_phase_a,rating_phase_b,rating_phase_c
Reference Sheet - 2. ODO Input Parameters
The parameters listed and described in the reference sheet - '2. ODO Input Parameters' These inputs are also user defined and are specified in the file called 'ODO_INPUT.XLSX'. In this document, the reference sheet '2. ODO Input Parameters' provides the definitions of all the inputs needed. The information in reference sheet 2 is for reference only and should not be updated.
Please update the corresponding input file 'ODO_INPUT.XLSX' as necessary. This file provides additional input parameters corresponding to user-defined constraints, investment options and time series data.
Reference Sheet - 3. Input JSON Syntax
As per the OD&O Repository on March 31st, 2019 (https://github.com/lanl-ansi/ODO), the ODO expected reduced power system models in JSON format. Users have two options to specify the inputs in the relevant format to be able to use OD&O tool:
1. Use the DiTTo Model conversion tool (https://github.com/risjain/ditto/tree/odo_tool) to generate the input JSON.
2. Develop user specific tools to generate the input JSON which will be used by the ODO Tool.
The network JSON thus generated is fed into the ODO tool along with the ODO_Input.xls file.
Reference sheet 3. "Input JSON Syntax" presents the input JSON structure and fields needed in the JSON file thus generated. This sheet will serve as a reference, if the users choose to develop their own tools to generate the input JSON files. For option 1) The ODO parser in DiTTo utilizes the system files to generate a compatible input network JSON for use with ODO tool.
Please refer to the respective repositories for instructions on installation and usage of the specific tools.

## 1. From the Model Files (JSON)
Component | Attribute | Units | Description | Default Values (Current) | (P)arsed from the System Model or (U)ser Input | File Location
Node (Buses) | name | String | Bus name |  | P
| nominal_voltage | Float | Nominal voltage at bus (phase-phase) | baseKV | P
| index | Integer | Unique bus index |  | P
| bus_type | Integer | The only valid values are 1, 2, 3, 4. 1 = PQ, 2 = PV, 3 = ref, 4 = isolated | Default =1. 3 if Source, 2 if generator attached | P
| vm | 3-value Float, p.u. | Minimum voltage magnitude (per unit) | [1.0, 1.0, 1.0] | P or U
| va | 3-value Float, radians | Maximum voltage magnitude (per unit) | [0.0, 0.0, 0.0] | P or U
| vmin | 3-value Float, p.u. | Minimum voltage magnitude (per unit) | [0.95, 0.95, 0.95] | P or U
| vmax | 3-value Float, p.u. | Maximum voltage magnitude (per unit) | [1.05, 1.05, 1.05] | P or U
| Microgrid | Integer | Identifies the circuit to which the given component is connected | 1 | P
| status | Integer | 1 if the bus is active, 0 if the bus is inactive | 1 | P or U
Generator | name | String | Name of the generator |  | P
| nominal_voltage | Float | Nominal voltage at bus (phase-phase) | baseKV | P
| pg | <3-value Float, p.u.> | Active power output from the generator (per phase) | [0.0, 0.0, 0.0] | P
| qg | <3-value Float, p.u.> | Reactive power output from the generator (per phase) | [0.0, 0.0, 0.0] | P
| gen_bus | Integer | Name of the bus to which the power source is connected. This can be interpreted as "from" at a feeder head and "to" for a PV inverter |  | P
| index | Integer | Unique generator index |  | P
| Microgrid | Integer | Identifies the circuit to which the given component is connected | 1 | P
| rg | Float | Internal resistance of the generator (p.u.) | 0 | P
| xg | Float | Internal reactance of the generator (p.u.) | 0 | P
| pmin | <3-value Float, p.u.> | Minimum real power output in pu | 0 | U
| pmax | <3-value Float, p.u.> | Maximum real power output in pu | pg | U
| qmin | <3-value Float, p.u.> | Minimum reactive power output in pu | -qg | U
| qmax | <3-value Float, p.u.> | Maximum reactive power output in pu | qg | U
| model | Integer | Generator cost model, 1 = piecewise linear, 2 = polynomial | 2 | U
| ncost | Integer | i.e 3 co-efficients for the polynomial | 3 | U
| cost | <3-value Float> | Parameters defining total cost function f(p) begin in this column, units of f(p) are $/hr and MW (or MVAr), respectively: (MODEL = 1) => p0, f0, p1, f1,..., pn, fn where p0 < p1 < ... < pn and the cost f(p) is defined by the coordinates (p0, f0), (p1, f1), . . . , (pn, fn) of the end/break-points of the piecewise linear cost. (MODEL = 2) => cn, ... , c1, c0 n + 1 coefficients of n-th order polynomial cost, starting with highest order, where cost is f(p) = c_n*p^n + ... + c1*p + c0 | [0.0, 0.0, 0.0] | U
| status | Integer | 0 = Inactive, 1 = Active | 1 | P or U
Line (Branches) | name | String | Line name |  | P
| nominal_voltage | Float | Nominal voltage at bus (phase-phase) | baseKV | P
| f_bus | Integer | From bus number |  | P
| t_bus | Integer | To bus number |  | P
| br_r | [<3-value Float, p.u.>, <3-value Float, p.u.>, <3-value Float, p.u.>] | Branch resistance in pu voltage (total for the line accounting for length) - This provides the matrix representation of the line impedance in complex form. Computed from the values of GMR and distances of individual wires. Kron reduction is applied to make this a 3x3 matrix. | [[0.0, 0.0, 0.0], [0.0, 0.0, 0.0], [0.0, 0.0, 0.0]] | P
| br_x | [<3-value Float, p.u.>, <3-value Float, p.u.>, <3-value Float, p.u.>] | Branch reactance in pu voltage (total for the line accounting for length) | [[0.0, 0.0, 0.0], [0.0, 0.0, 0.0], [0.0, 0.0, 0.0]] | P
| g_fr, g_to, b_fr, b_to | <3-value Float, p.u.>, each of these | Total line charging conductance and susceptance in p.u. | [0.0, 0.0, 0.0] | P
| shift | <3-value Float> | transformer phase shift angle (degrees), positive implies delay | [0.0, 0.0, 0.0] | P
| transformer | Bool | True if the branch is a transformer, False if it is a line | FALSE | P
| current_rating_a | <3-value Float, p.u.> | Rated currents of each phase of the branch. Wires->ampacity only for ABC | [1.0, 1.0, 1.0] | P or U
| index | Integer | Unique branch index |  | P
| angmin | <3-value Float, radians> | Minimum angle difference, theta_f - theta_t | [-1.0472, -1.0472, -1.0472] | P or U
| angmax | <3-value Float, radians> | Maximum angle difference, theta_f - theta_t | [1.0472, 1.0472, 1.0472] | P or U
| Microgrid | Integer | Identifies the circuit to which the given component is connected | 1 | P
| current_rating_a | <3-value Float, p.u.> | Rated currents of each phase of the branch. Wires->ampacity only for ABC | [0.0, 0.0, 0.0] | P or U
| angmin | <3-value Float, radians> | Minimum angle difference, theta_f - theta_t | [-1.0472, -1.0472, -1.0472] | P or U
| angmax | <3-value Float, radians> | Maximum angle difference, theta_f - theta_t | [1.0472, 1.0472, 1.0472] | P or U
| status | Integer | initial branch status, 1 = in-service, 0 = out-of-service | 1 | P or U
Load | name | String | Name of the load |  | P
| nominal_voltage | Float | Nominal voltage at bus (phase-phase) | baseKV | P
| pd | <3-value Float, p.u.> | Real power demand in per unit (one value per phase) - at a snapshot defined in the original model | [0.0, 0.0, 0.0] | P
| qd | <3-value Float, p.u.> | Reactive power demand in per unit (one value per phase) - at a snapshot defined in the original model | [0.0, 0.0, 0.0] | P
| load_bus | Integer | Name of the bus the load is connected to | 1 | P
| Microgrid | Integer | Identifies the circuit to which the given component is connected | 1 | P
| critical | Integer | Load Criticality Index (from 0 to N), where N is the number of criticality categories specified by the user | 0 | P or U
| status | Integer | Load status; = 1 if connected | 1 | P or U
PowerSource (Slack Bus) | name | String | Name of the power source (Substation Bus) |  | P
| baseKV | Float | This parameter defines the base voltage at the power source. | 12.47 | P or U
| baseMVA | Float | This parameter defines the base MVA of the power source. | 10 | P or U
| Microgrid | Integer | Identifies the circuit to which the given component is connected | 1 | P
| per_unit | bool | Yes/No | TRUE | U
| conductors | int | Number of conductors | 3 | P or U
Storage | name | String | Storage name |  | P
| storage_bus | Integer | Name of the bus the storage is connected to. |  | P
| nominal_voltage | Float | Nominal voltage at bus (phase-phase) | baseKV | P or U
| r | <3-value Float, p.u.> | Equivalent percent internal resistance. In ohms. | [0.1, 0.1, 0.1] | P
| x | <3-value Float, p.u.> | Equivalent percent internal reactance. In ohms. | [0.0, 0.0, 0.0] | P
| index | Integer | Unique storage index |  | P
| Microgrid | Integer | Identifies the circuit to which the given component is connected | 1 | P
| current_rating | <3-value Float, p.u.> | Rated power of the device. | [0.0, 0.0, 0.0] | U
| qmin | <3-value Float, p.u.> | Minimum reactive power of the device | [-1.0, -1.0, -1.0] | U
| qmax | <3-value Float, p.u.> | Maximum reactive power of the device | [1.0, 1.0, 1.0] | U
| energy_rating | Float, p.u. | Rated storage capacity | 1 | U
| energy | Float, p.u. | Present amount of energy stored | 1 | U
| discharge_rating | Float, p.u. | Discharge rate in percent of rated power. | 50 | U
| charge_rating | Float, p.u. | Charging rate in percent of rated power. | 70 | U
| charge_efficiency | Float, p.u. | Percent efficiency for charging the storage element. | 1 | U
| discharge_efficiency | Float, p.u. | Percent efficiency for discharging the storage element. | 1 | U
| standby_loss | Float, p.u. | Standby Loss of the Storage Unit | 0 | U
| status | Integer | 0 = Inactive, 1 = Active | 1 | P or U
Shunt | name | String | Name of the Shunt Bank |  | P
| nominal_voltage | Float | Nominal voltage at bus (phase-phase) | baseKV | P
| shunt_bus | Integer | The name of the node that the capacitor connects to |  | P
| gs |  | Computed from var values and nominal_voltage for each phase | 0.001 | P
| bs |  | Computed from var values and nominal_voltage for each phase | 0.001 | P
| index | Integer | Unique storage index |  | P
| Microgrid | Integer | Identifies the circuit to which the given component is connected | 1 | P
| status | Integer | 0 = Inactive, 1 = Active | 1 | P or U
Transformers (Branches) | name | String | Transformer name |  | P
| shift | <3-value Float> | transformer phase shift angle (degrees), positive implies delay | [0.0, 0.0, 0.0] | P
| f_bus | Float | Name of the node which connects to the 'from' end of the transformer |  | P
| t_bus | Float | Name of the node which connects to the 'to' end of the transformer |  | P
| br_x | [<3-value Float, p.u.>, <3-value Float, p.u.>, <3-value Float, p.u.>] | Branch reactance in pu (total for the transformer) | [[0.0, 0.0, 0.0], [0.0, 0.0, 0.0], [0.0, 0.0, 0.0]] | P
| br_r | [<3-value Float, p.u.>, <3-value Float, p.u.>, <3-value Float, p.u.>] | Branch resistance in pu (total for the transformer) | [[0.0, 0.0, 0.0], [0.0, 0.0, 0.0], [0.0, 0.0, 0.0]] | P
| nominal_voltages | [<2-value Float>] | Nominal voltage at bus (phase-phase) - high/low | baseKV | P
| tap | <3-value Float> | Transformer off nominal turns ratio, taps at 'from' bus, impdedance at 'to' bus, i.e., if r = x = b = 0, tap = mag(Vf)/mag(Vt.). Read from Windings->Phase_windings->taps | [1.0, 1.0, 1.0] | P
| current_rating_a | <3-value Float, p.u.> | Rated currents of each phase of the transformer (winding->rated power) | [1.0, 1.0, 1.0] | P
| Windings | <string, string> | Winding type (Wye/Delta/Zig-zag) for the HV and LV sides |  | P
| angmin | <3-value Float, radians> | Minimum angle difference, theta_f - theta_t | [-1.0472, -1.0472, -1.0472] | P or U
| angmax | <3-value Float, radians> | Maximum angle difference, theta_f - theta_t | [1.0472, 1.0472, 1.0472] | P or U
| index | Integer | Unique branch index |  | P
| transformer | Bool | True if the branch is a transformer, False if it is a line | TRUE | P
| g_fr, g_to, b_fr, b_to | <3-value Float, p.u.>, each of these | Total transformer charging conductance and susceptance in p.u. | [0.001, 0.001, 0.001] | P
| Microgrid | Integer | Identifies the circuit to which the given component is connected | 1 | P
| status | Integer | initial branch status, 1 = in-service, 0 = out-of-service | 1 | P or U

## 2. ODO Input Parameters
Worksheet | Parameters/Data Requirements | Description | Remarks
RunSettings | MaxTime (seconds) | Maximum Simulation Run time for analysis by OD&O
| MaxIterations | Maximum Iteration limit
| Tolerance | Error Tolerance
| Number of Years | Number of Years for the Scope of Analysis
| Inflation Rate | Rate of Inflation over the years (%)
| Demand Growth Rate | Rate of the growth of Power demand over the years (%)
| Networked | Yes/No Flag - Indicates if the user wants to run the tool in networked mode or not
PvWindInvest | MinCapacity (kW) | Minimum installed Capacity at the given node | For both Wind and PV - Specified at each node
| MaxCapacity (kW) | Maximum installed Capacity at the given node
| ExistingCapacity (kW) | Existing installed Capacity at the given node
| Age (years) | Age of the existing/installed asset
DieselInvest | node | Bus to which the asset is connected | Type of the Generator is not specified in the JSON file. This input sheet specifies which of the system generators are Diesel based
| TechNo | Technology Identifier
| MinAnnualHours | Minimum Hours of Operation for the Diesel Gen
| MaxAnnualHours | Maximum Hours of Operation for the Diesel Gen
| MinLoad (kWh) | Minimum Load on the Diesel Gen
Min (number of units)
Max (number of units)
| Existing (0/1) | Is it already installed?
| Age (years) | Age of the existing/installed asset
BattInvest | node | Bus to which the asset is connected
| BattInverterType | Inverter Identifier
Min (number of units)
Max (number of units)
| Existing (0/1) | Is it already installed?
| Age (years) | Age of the existing/installed asset
BranchInvest | Symmetrical matrix mapping the from and to nodes of the branches which can be strengthended |  | ODO may suggest line hardening by adding parallel lines between the nodes as needed.
SwitchInvest | Symmetrical matrix mapping the from and to nodes of the Switches which can be strengthended
PvWindParams | PvCapCost ($/kW) | Capital Cost
| PvEff | Efficiency
| WindCapitalCost ($/kW) | Capital Cost
| WindEff | Efficiency
BattParams | BattInverterType | Inverter Technology Identifier (Name)
| MaxS (kW) | Rating
| lifetime (years) | Rated Lifetime
| Capcost ($/kW) | Capital Cost
| effCoef_x1 | Coordinates of the breakpoints corresponding to the piece-wise linear efficiency curve of a battery.
effCoef_y1
effCoef_x2
effCoef_y2
effCoef_x3
effCoef_y3
effCoef_x4
effCoef_y4
effCoef_x5
effCoef_y5
| Phases (1,2,3) | Shows which phases is the given battery type connected to | 1: Phase A, 2: Phase B, 3: Phase C
DieselParams | TechNo | Technology Identifier
| Description | Name
| MaxS (kW) | Rating
| Capcost ($) | Capacity Cost
| cost0 ($/kwh) | c0 + (c1*pg) + (c2*pg^2) where pg is real power output
cost1 ($/kwh)
cost2 ($/kwh)
| Type | Type of the Diesel Gen
| efficiency | Percentage Efficiency
| MaxRampUp | Ramp rates
MaxRampDown
| lifetime (years) | Life of the Asset
| Phases (1,2,3) | Shows which phases is the given Diesel generator type connected to | 1: Phase A, 2: Phase B, 3: Phase C
CableParams | CableNo | Cable name
Description
| Capcost ($/km) | Capacity Cost
Resistance (Ohms/km)
Reactance (Ohms/km)
Rating (Amps)
| Phases (1,2,3) | Shows which phases is the given cable type connected to | 1: Phase A, 2: Phase B, 3: Phase C
SwitchParams | SwitchNo | Switch Identifier
Description
Cost ($)
| Remote (0/1) | Can the switch be remotely operated?
| Protection (0/1) | Is the switch associated with a protection relay?
| Phases (1,2,3) | Shows which phases is the given switch type connected to | 1: Phase A, 2: Phase B, 3: Phase C
CableLen | Upper triangular matrix specifying the length of the cable between the given nodes
MonthSeason | Classifying each month as a Summer/Winter month
NumberOfDays | peak | Classifying the number of days corresponding to each of these categories (peak/week/weekend) for all 12 months
week
weekend
SolarAverage | Irrandiance (kW/m2)
| 1 | Monthly Hour-Average Irradiance during the day for all 12 months
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
SolarVariance | Irrandiance (kW/m2)
| 1 | Variance in the Monthly Hour-Average Irradiance during the day for all 12 months
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
WindAverage | WindSpeed (mph)
| 1 | Monthly Hour-Average Wind Speed during the day for all 12 months
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
WindVariance | WindSpeed (mph)
| 1 | Variance in the Monthly Hour-Average Wind Speed during the day for all 12 months
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
Non-branch Entity Reliability | Tabulated failure rates of all the non-branch components in the system | Value x 100 = Percentage failure rate of the given component
Branch Reliability | Upper Triangular matrix mapping the from and to nodes of the branches - with the respective entries being the probability of the failure for the given line. | Value x 100 = Percentage failure rate of the given branch
Resiliency Scenarios | Table summarizing the different damage scenarios for which the system reliability will be evaluated. This marks the failures of line and other components for an outage scenario, that the networked microgrid will be expected to perform reliably under
LoadTimeSeries | Hourly profiles for all the loads (per phase) in the given system organized as - Time, load_1_phase_i, load_2_phase_j, and so on |  | The values are complex numbers (p + j.q) - for each phase. Therefore, the 3 phase loads will need to be scaled accordingly to distribute into the respective 'single' phase profiles